## Slide 1
SPE AFRICA GEOTHERMAL DATATHON 2026
Integrated Geothermal District Heating
& Cooling System for Utrecht, Netherlands
10.5 MWth
Heating
5.0 MWth
Cooling
€74/MWh
LCoE
TEAM GEOLOGIC ANALYTICS
Uadia Moses Imoukhedeh SPE 5174626
Ogundimu Samuel Oluwaseun SPE 5408045
Akanmu Oluwaseun Emmanuel SPE 5436014
Adejor Friday Emmanuel SPE 5510461
Favour Ifeanyichukwu Ogboi SPE 5898562
Team_GeoLogicAnalytics_PPT_V1

## Slide 2
PROBLEM FRAMING
The Challenge & Our Central Insight
The brief demands a coherent system — not a single well — delivering firm heating and cooling, sustainably and economically, from a medium-temperature aquifer.
10 MWth Heating
From a low-enthalpy reservoir (70–77 °C).
5 MWth Cooling
Year-round, balanced seasonally.
Low-Carbon
Minimise fossil & grid electricity.
Flexibility
Bridge constant supply vs seasonal demand.
OUR CENTRAL INSIGHT
Transmissivity beats temperature.
For a low-enthalpy resource, the fluid volume the reservoir delivers matters more than how hot it is. A hot but tight well produces no usable power.
PKP-01: 88 °C but 0.1 Dm → not viable
2
GeoLogic Analytics · SPE Africa Geothermal Datathon 2026

## Slide 3
METHODOLOGY
From Raw Logs to a Bankable System
01
Data Engineering
Ingest & QC four well logs; validate depths; engineer petrophysical features
→
02
Resource Screening
Rank candidates on transmissivity; scout ThermoGIS corridors
→
03
System Design
Size heat exchanger, heat pump, chiller, ATES & storage
→
04
Economics & Risk
Depth-based CAPEX, LCoE & 10,000-run Monte Carlo
Engineering rigour and evaluation discipline come before architectural complexity — every parameter is traceable to data or the surface design report.
3
GeoLogic Analytics · SPE Africa Geothermal Datathon 2026

## Slide 4
EDA · FINDING 01
Data Engineering: Getting the Basics Right
Missing-data audit — −999.25 null sentinel detected & flagged
MD vs TVD — depth correction for the deviated well
Three quiet errors most teams will carry forward:
Caught a hidden null code
The −999.25 sentinel was mapped to true missing values before any statistics were computed.
Caught a labelling error
A ThermoGIS sheet headed “PKP-01” carried BLT-01 coordinates — flagged and corrected before screening.
Caught the depth trap
Target depths in along-hole MD were converted to TVD via the well-path survey — or every temperature estimate would be wrong.
4
GeoLogic Analytics · SPE Africa Geothermal Datathon 2026

## Slide 5
EDA · FINDING 02
Transmissivity Drives Viability
Transmissivity ranking across all targets
Viability trade-space — bubble size ∝ thermal power
31.1 Dm
REINJ-01 — best in class
PKP-01
88 °C but 0.1 Dm → useless
5
GeoLogic Analytics · SPE Africa Geothermal Datathon 2026

## Slide 6
EDA · FINDING 03
Final Subsurface Architecture
Well
Role
Temp °C
Flow m³/h
Trans. Dm
BLT-01
Validated Production
77
105
9.3
GLA-01
Optimised Corridor
70
140
15.2
GLA-02
Backup / Contingency
71
132
13.4
REINJ-01
Reinjection Corridor
55
192
31.1
Production doublet: BLT-01 + GLA-01 deliver 245 m³/h of blended 73 °C brine. GLA-02 is held in reserve. REINJ-01 — the highest-injectivity corridor at 31.1 Dm — safely accepts the cooled brine and maintains reservoir pressure.
GLA-01 — ThermoGIS Evidence
6
GeoLogic Analytics · SPE Africa Geothermal Datathon 2026

## Slide 7
SYSTEM DESIGN · FINDING 04
System Architecture at a Glance
Hot brine / heating
Cooling / aquifer
Electricity (solar)
Geothermal Doublet
BLT-01 + GLA-01 → 245 m³/h of 73 °C brine
Energy Centre
Heat exchanger + heat-pump upgrade to 70 °C
Thermal Storage
ATES seasonal wells + hot & cold buffer tanks
Solar Powered
1.5 MW PV drives the heat pump & chiller
7
GeoLogic Analytics · SPE Africa Geothermal Datathon 2026

## Slide 8
SYSTEM DESIGN · FINDING 05
Thermodynamics of the Production Loop
BLT-01
77 °C · 105 m³/h
30.33 kg/s
GLA-01
70 °C · 140 m³/h
40.44 kg/s
+
BLENDED PRODUCTION
73 °C · 70.78 kg/s
Total geothermal power
Q = ṁ · Cp · ΔT = 70.78 × 4.0 × (73 − 37.5)
Q ≈ 10.05 MWth
Geothermal
10.05 MWth
→
+ Heat pump
0.45 MWth
→
= Delivered
10.5 MWth
Honest engineering: geothermal supply (10.05 MWth) and the heat-pump upgrade (0.45 MWth) together meet the 10.5 MWth heating target — comfortably above the 10 MW minimum. The heat pump is the engineered bridge from a low-enthalpy aquifer to a usable district supply temperature.
8
GeoLogic Analytics · SPE Africa Geothermal Datathon 2026

## Slide 9
SYSTEM DESIGN · FINDING 06
Energy Centre, Storage & Renewable Integration
Titanium Heat Exchanger
Separates corrosive brine from the clean district loop.
Heat Pump (COP ≈ 2.25)
Upgrades 68→70 °C; +0.45 MWth on 0.2 MW electric.
ATES Seasonal Wells
Warm 15–35 °C, cold 8–15 °C — shifts heat & cold across seasons.
Buffer Tanks
Hot 575 m³/20 MWh + cold 1,225 m³/10 MWh shave 4-hr peaks.
Mechanical Chiller
5 MWth cooling at 7/15 °C; rejects to ATES cold well.
1.5 MW Solar PV
Covers all parasitic load (1.2 MW) — renewably self-sufficient.
Two-tier storage (seasonal ATES + daily buffer tanks) lets the wells run near-constant at their efficient point, decoupling continuous supply from seasonal demand.
9
GeoLogic Analytics · SPE Africa Geothermal Datathon 2026

## Slide 10
SYSTEM DESIGN · FINDING 07
Seasonal Demand & Annual Dispatch
Monthly heating & cooling demand vs capacity
Integrated monthly dispatch — geothermal + storage + minimal backup
>95 %
Demand met by geothermal + storage
10.5 MWth
Firm heating, every winter month
5.0 MWth
Firm cooling through summer peak
10
GeoLogic Analytics · SPE Africa Geothermal Datathon 2026

## Slide 11
ECONOMICS · FINDING 08
Capital Cost & Levelised Cost of Energy
CAPEX composition (left) and annual operating costs (right)
Depth-based drilling: each of 5 wells costed by its own depth — BLT-01 (1,700 m), GLA-01 (1,642 m), REINJ-01 (1,211 m), 2 ATES wells (150 m). Total drilling €25.5 M.
€41.0 M
Total capital expenditure
€74.4/MWh
Base-case LCoE (EU range)
€1.23 M/yr
Annual operating cost
11
GeoLogic Analytics · SPE Africa Geothermal Datathon 2026

## Slide 12
ECONOMICS · FINDING 09
Uncertainty: 10,000-Run Monte Carlo
Probabilistic LCoE distribution (10,000 simulations)
Tornado sensitivity — ±20 % on each parameter
P10
€67
/MWh
P50
€80
/MWh
P90
€95
/MWh
Why this matters: a single LCoE hides risk. Even at P90 the system stays within the EU district-heating range — robust, not just optimistic.
12
GeoLogic Analytics · SPE Africa Geothermal Datathon 2026

## Slide 13
CRITICAL APPRAISAL · FINDING 10
Limitations & Key Assumptions
We state our boundaries plainly — a credible design is one whose limits are understood.
Known Limitations
• No coupled reservoir simulation — steady-state flow assumed; thermal drawdown over time not modelled.
• GLA-01 is a hypothetical target — not an existing well — new drilling carries delivery uncertainty.
• Simplified demand profiles — no hourly district consumption data within the challenge framework.
• ThermoGIS P50 used deterministically — full probabilistic reservoir coupling not implemented.
• ATES integration is conceptual — no groundwater-flow simulation performed.
Key Assumptions
Brine properties: ρ = 1040 kg/m³ · Cp = 4.0 kJ/kg·K
Reinjection temperature: 35–40 °C after heat extraction
District regime: 70 °C supply / 40 °C return
Heat pump COP: 2.25 (68→70 °C upgrade)
Economic lifetime: 15 years, 6 % discount rate
Demand basis: 10 MWth heat / 5 MWth cool (minimums)
13
GeoLogic Analytics · SPE Africa Geothermal Datathon 2026

## Slide 14
DIFFERENTIATION
Why This Submission Stands Out
Data-engineering rigour
TVD depth correction, hidden-null detection and a caught label error — quiet mistakes most teams carry forward.
True system integration
Geothermal + reinjection + heat pump + chiller + ATES + buffer tanks + solar — a complete energy system, not a single well.
Uncertainty-aware economics
A full Monte Carlo risk profile (P10/P50/P90), not a single hopeful LCoE — the language investors trust.
Honest, defensible engineering
We state plainly that geothermal + heat pump together meet 10.5 MWth, framing the margin as deliberate efficient design.
14
GeoLogic Analytics · SPE Africa Geothermal Datathon 2026

## Slide 15
Conclusions & Recommendations
Utrecht can be supplied with firm, low-carbon district heating and cooling from a low-enthalpy aquifer — delivered by rigorous data engineering, integrated thermal design, and economics that survive scrutiny under uncertainty.
Drill an appraisal well at GLA-01 — Convert the hypothetical corridor to a proven producer before final investment — the single biggest uncertainty.
Acquire hourly demand data — Replace the simplified seasonal profile with metered consumption to refine storage sizing.
Run a coupled reservoir + ATES model — Quantify thermal drawdown and groundwater interaction over the 30-year life.
10.5 / 5.0
MWth heat / cool
€74/MWh
Base-case LCoE
>95 %
Geothermal share
Team GeoLogic Analytics · SPE Africa Geothermal Datathon 2026